ISQB Specification

TYPICAL SPECIFICATIONS

Model: ISQB

Description: Fan shall be of the “Square in-line” type with a square inlet and outlet. Fan shall be designed for floor mount or hung installations in-line with ducting, and have a belt driven centrifugal wheel. Fan shall be a corrosion resistant steel, belt driven, square inline blower.

Application: Square In-Line Duct Blowers are suitable for various applications. Commonly mounted indoors with both inlet and outlet ducts to supply or exhaust air. Square In-Line Duct Blowers are engineered to discharge air, fumes and other contaminants horizontally in a duct.

Certifications: Square In-line Duct Blower(s) shall be licensed to bear the AMCA Certified Ratings Seal for Air and Sound Performance and be ETL Listed to UL705 Standards.

Construction: Square In-line Duct Blower(s) shall be constructed of steel with corrosion resistant, high solids, enamel finish. A removable cover shall provide blower motor access, and drive access shall be provided on both sides through removable panels. Blowers shall be belt driven; centrifugal backward inclined, with cast iron pillow block, regreaseable ball bearings having a minimum L50 (average) life of 200,000 hours. The shaft shall be keywayed at both ends.

Drives are to be selected for 150% of driven horsepower. Blower pulley shall be fixed, machined, cast iron. Motor pulley shall be cast iron, variable speed.

Housing

The blower shell shall be constructed of welded corrosion resistant steel with high solids and enamel finish. Side panels shall be removable for service access.

Wheel

Centrifugal type with 100% steel backward inclined blades. Balanced in accordance with AMCA standard 204-96, Balance Quality and Vibration Levels for Fans.

Motor & Motor Compartment

Motor shall have permanently lubricated ball bearings and be of voltage, phase, and enclosure as specified. A motor cover shall be supplied as standard.

Shaft and Bearings

Shafts shall be precision ground and polished. Bearings, selected specifically for air handling duty, and of the pillow block relubricatable type, shall be selected to have a predicted L50 life of not less than 200,000 hours at maximum cataloged operating speed.

Belts & Drives

Belts and drives shall be sized for a minimum of 150% of the driven BHP. Drives shall be of cast iron and keyed to the shafts.

Product: Fan shall be model ISQB as manufactured by CaptiveAire Systems.